## Repair Points
UH Air Handler Inspection Checklist
Marketing Plan Lists
HAHU -
Task | Need Y/N | Suggested Replacement Brand Model | Contractor Proposed Brand & Model / Comments
Main PH Valve |  | Series 45114 150# Flanged Cast Steel Globe Valve / or equivalent
Main CW Valve |  | Series 45114 150# Flanged Cast Steel Globe Valve / or equivalent
Main Steam Valve |  | Jomar Valve T-100SSS Series FNPT Brass Ball Valve w/Steam Trim / or equivalent
CW Coil Valves |  | American Valve 4000 Series / or equivalent
PH Coil Valve |  | American Valve 4000 Series / or equivalent
Steam Coil Valve |  | Jomar Valve T-100SSS Series FNPT Brass Ball Valve w/Steam Trim / or equivalent
PH Blow Down Valve |  | Equivalent or better than originally installed
CW Blow Down Valve |  | Equivalent or better than originally installed
Steam Blow Down Valve |  | Equivalent or better than originally installed
Steam Traps |  | Equivalent or better than originally installed
AHU Stainers |  | Equivalent or better than originally installed
AHU CW JCI Valve |  | JCI
AHU PH JCI Valve |  | JCI
AHU Steam JCI Valve |  | JCI
AHU Discharge Air Temp Sensor |  | JCI
AHU Preheat Temp Sensor |  | JCI
AHU Return Air Temp Sensor |  | JCI
AHU Humidity Sensor |  | JCI
AHU JCI Start / Stop Switch |  | JCI
AHU Preheat Temp Sensor |  | JCI
AHU Damper Linkage / Motor |  | JCI
Return Air Damper |  | Equivalent or better than originally installed
AHU Floor Drains |  | Equivalent or better than originally installed
AHU Box Repairs (Metal Repairs) |  | Equivalent or better than originally installed
AHU Doors |  | Equivalent or better than originally installed
BMS intergation |  | JCI
AHU Box Epoxy |  | Encon Metaclad Epoxy or equivalent
AHU Motor |  | Equivalent or better than originally installed
AHU Belts |  | Equivalent or better than originally installed
AHU Belt Guard |  | Equivalent or better than originally installed
AHU Freezestats |  | JCI
AHU Electrical Boxes |  | Equivalent or better than originally installed
All fire alarm system inegration |  | Alarm & Communication Technologies (Vendor)
AHU End Switch |  | JCI
AHU Insulation |  | Equivalent or better than originally installed
AHU Shaft |  | Equivalent or better than originally installed
AHU Shaft Bearings |  | Equivalent or better than originally installed
AHU Magnahelic Meter |  | Dwyer SERIES 2000 MAGNEHELIC or Equivalent
AHU Pulleys |  | Equivalent or better than originally installed
AHU PH Coils |  | Equivalent or better than originally installed
AHU CW Coils |  | Equivalent or better than originally installed
AHU Steam Coils |  | Equivalent or better than originally installed
AHU Motor Bearing |  | Equivalent or better than originally installed
Go to HAHU Information

## Air Handler List
UH Air Handler Unit List
AIR HANDLER | MOTOR | DESIGN CFM | BEARING / BELT | AREA SERVING
HAH 1 | 100 HP / FR. 404 T 480V 3PH | 56,000 CFM / 1030 RPM | FAN BRG. PLB6871PH3 / MOTOR BRG. PLB6839HX3 / 5V1900 | C level Main Lobby / Blood Bank / Super Track / Registration / Mezzanine
HAH 2 | 40 HP / FR. 324T 480V 3PH | 23640 CFM / 1215 RPM | FAN BRG. PLB6847RH / MOTOR BRG. PLB6827FX3 / CX120 | C Level Labs / Hematology Labs / Blood Bank / Ortho / Fast track
HAH 3 | 40 HP / FR. 324T 480V 3PH | 17350 CFM / 2120 RPM | BX 112 | Emergency Department / Radiology
HAH 4 | 30 HP / FR. 286T 480V 3PH | 14910 CFM / 2000 RPM | FAN BRG. FAFNIR / MOTOR BRG. FAFNIR / BX90 | ER Pediatrcis / Dental Clinic
HAH 5 | 70 HP / FR. 365T 480V 3PH | 46500 CFM / 1080 RPM | FAN BRG. PLB6863PH3 / MOTOR BRG. 9344890HX3 / 5V1500 | Kitchen
HAH 6 | 10 HP / FR. 215T 480V 3PH | 6500 CFM / 2650 RPM | FAN BRG. SF23TC /MOTOR BRG. F106 / B85 | Microbiology Lab
HAH 7 | 40 HP / FR. 324T 480V 3PH | 18130 CFM / 1640 RPM | FAN BRG. PLB6847RH / MOTOR BRG. PLB6827FX3 / CX120 | A Level Support Services / Call Center / Security Office
HAH 8 | 15 HP / FR. 254T 480V 3PH | 9500 CFM / 1896 RPM | FAN BR. SF27IC / MOTOR BRG. F106 / B85 | A Level Electrical vault
HAH 9 | 100 HP / FR. 404T 480V 3PH | 49210 CFM / 1123 RPM | FAN BRG, SAF513 / MOTOR BRG. SAF522 / 5V1700 | Main Pharmacy / Radiology Office / Pharmacy Office / B Level Hall Ways / EVS
HAH 10 | 50 HP / FR. 326T 480V 3PH | 25900 CFM / 1490 RPM | FAN BR. LINK BELT / MOTOR BRG. LINK BELT / CX120 | A level Office Space / B Level Office Space
HAH 11 | 30 HP / FR. 286T 480V 3PH | 18100 CFM / 1909 RPM | FAN BRG, PB22447H2 / MOTOR BRG. N5116MP5 / B103 | Respiratory Offices / Central Sterile / Physical Therapy
HAH 12 | 20 HP / FR. 256T 480V 3PH | 11400 CFM / 890 RPM | FAN BRG. FAFNIR / MOTOR BRG. FAFNIR / BX90 | HR / Medical Records
HAH 13 | 10 HP / FR. 215T 480V 3PH | 6500 CFM / 2650 RPM | FAN BRG. SF271C / MOTOR BRG. F106 / B77 | G417-G422 / G318-G322 / G217-G221
HAH 14 | 30 HP / FR. 286T 480V 3PH | 16800 CFM / 1894 RPM | FAN BRG. PB2247H / MOTOR BRG. RHPMP5 / B112 | OR 1 2 6
HAH 15 | 25 HP / FR 284T 480V 3PH | 12300 CFM / 1794 RPM | FAN BRG. PB22667H / MOTOR BRG. TBD / BX93 | OR 3 5
HAH 16 | 25 HP / FR 284T 480V 3PH | 12300 CFM / 1794 RPM | FAN BRG. LAO / MOTOR BEARING TBD / BX93 | OR 7 8 12
HAH 17 | 30 HP / FR. 286T 480V 3PH | 17400 CFM / 1625 RPM | FAN BRG. LINK BELT / MOTOR BRG. MSPD27 / B112 | OR 9 10 11
HAH 18 | 125 HP / FR. 405T 480V 3PH | 67500 CFM / 1107 RPM | FAN BRG. LINK BELT 315116 / MOTOR BRG, MSPD27 / 5V1900 | Wound Care / Pain Management / F Orange Office Space / Employee Health / Neuro Labs / Nuclear Medicine / Cath Lab Main Spaces / Cath Lab 2
HAH 19 | 25 HP / FR 284T 480V 3PH | 14300 CFM / 1756 RPM | FAN BRG. SFK SYR / MOTOR BRG. MSPD27 / B108 | L&D / L&D OR 4 / FICN
HAH 20 | 25 HP / FR 284T 480V 3PH | 15000 CFM / 1778 RPM | FAN BRG. SFK SYR / MOTOR BRG. MSPD27 / B108 | L&D / L&D OR 1-3
HAH 21 | 125 HP / FR. 405T 480V 3PH | 66500 CFM / 1007 RPM | FAN BRG. LINK BELT / MOTOR BEARING PLB6931HX3 / 5V1900 | Center Core Hallways, Offices & Elevator Lobby D Level - I Level
HAH 22 | 100 HP / FR. 404T 480V 3PH | 57500 CFM / 1011 RPM | FAN BRG. PLB6871HX33 / PLB6839HX3 / 5V1900 | E Green Offices / D Green / F Green / G Green / H Green
HAH 23 | 100 HP / FR. 404T 480V 3PH | 64700 CFM / 940 RPM | FAN BRG. TBD / MOTOR BRG. PLB6843HX3 / 5V1900 | D Yellow / E Yellow / F Yellow / G Yellow / H Yellow / I 316 - I322
HAH 24 | 60 HP / FR. 364T 480V 3PH | 38000 CFM / 1224 RPM | FAN BRG. SF23TC /MOTOR BRG. F106 / CX150 | C Suite / E Blue / F Blue - I Blue Nurses Station & Hallways
HAH 25 | 10 HP / FR. 215T 480V 3PH | 5000 CFM / 2450 RPM | FAN BRG. SF23TC / MOTOR BRG. F106 / B42 | SICU / E Green Office Space
HAH 26 | 10 HP / FR. 215T 480V 3PH | 5000 CFM / 2450 RPM | FAN BRG. SF23TC / MOTOR BRG. F106 / B77 | PACU
HAH 27 | 20 HP / FR. 256T 480V 3PH | 14000 CFM / 1615 RPM | FAN BRG. SKF SYR / MOTOR BRG. SM RNPMP5 / BX | K Level / J Level
HAH 28 | 60 HP / FR. 364T 480V 3PH | 70000 CFM / 504 RPM | FAN BRG. PLB6863FH3 / MOTOR BRG. PLB6831H / CX240 | Loadin Dock
HAH 30 | TBD | TBD | TBD | Trauma
HAH 31 | TBD | TBD | TBD | Emergency Department Entrance
HAH 32 | TBD | TBD | TBD | Main Entrance
HAH 33 | TBD | TBD | TBD | ICU 1
HAH 34 | TBD | TBD | TBD | ICU 2
HAH 35 | TBD | TBD | TBD | D Blue - I blue Patient Rooms
HAH 37 | TBD | TBD | TBD | OR 4
HAH 38 | TBD | TBD | TBD | OR Back up unit
HAH M | TBD | TBD | TBD | Mezzanine
HAH Cath 3 | TBD | TBD | TBD | Cath Lab 3 / Cath Lab Hallway
HAH M | TBD | TBD | TBD | Mezzanine
ACC AHU 1 | TBD | TBD | TBD | ACC
ACC AHU 2 | TBD | TBD | TBD | ACC
ACC AHU 4 | TBD | TBD | TBD | ACC
ACC AHU 5 | TBD | TBD | TBD | ACC
Stone Center AHU 1 | TBD | TBD | TBD | Stone Center
Go to HAHU Checklist